# FluxGen Modbus IoT Gateway

Complete Project Report

Company: FluxGen Technologies

Project Lead: Chaithu Reddy

Report Date: March 26, 2026

Duration: November 2025 - March 2026 (5 months)

Current Version: v1.3.8

Total Commits: 255

Codebase: 25,787 lines of C code across 31 source files

# 1. What is This Project?

The FluxGen Modbus IoT Gateway is an industrial IoT device built on the ESP32 microcontroller. It sits between industrial sensors (flow meters, water quality analyzers) and the cloud (Azure IoT Hub).

## What It Does (Simple Explanation)

Water Pipe                    Internet                     Dashboard
     │                            │                            │
  ┌──┴──┐    RS485 Cable    ┌─────┴─────┐   WiFi / 4G   ┌────┴────┐
  │Flow │ ───────────────── │  FluxGen  │ ──────────── │  Azure  │
  │Meter│   Modbus Protocol │  Gateway  │  MQTT/TLS    │  Cloud  │
  └─────┘                   └───────────┘              └─────────┘
                                 │
                            ┌────┴────┐
                            │ SD Card │ (offline backup)
                            └─────────┘

Reads sensors every 5 minutes using RS485 Modbus protocol

Sends data to cloud via Azure IoT Hub (MQTT over TLS)

Stores data offline on SD card if internet is down

Replays cached data automatically when internet returns

Configurable remotely via Azure Device Twin or locally via web browser

Updates firmware remotely via OTA from GitHub releases

## Who Uses It

Water utilities monitoring flow rates

Industrial sites monitoring water quality (pH, TDS, Temperature)

Residential complexes tracking water usage at overhead tanks

# 2. Why We Built It

## Problem

Industrial sensors (flow meters, water quality analyzers) output data over RS485 Modbus — a 40-year-old protocol. Getting this data to a cloud dashboard requires:

A device that speaks Modbus RTU

Internet connectivity (WiFi or cellular)

Reliable data delivery (no data loss during outages)

Remote management (can't send technicians to every site)

Easy field configuration (non-technical staff need to set it up)

## Solution

A single, compact ESP32-based gateway that:

Reads any Modbus RTU sensor (configurable via web UI)

Connects via WiFi OR 4G cellular

Caches data on SD card during outages

Receives remote configuration and firmware updates

Costs under $15 in hardware components

## Why ESP32?

| Requirement | ESP32 Capability |
| --- | --- |
| Dual connectivity | WiFi built-in + UART for 4G modem |
| Real-time sensor reading | Dual-core 240MHz, FreeRTOS |
| Low power | Deep sleep capable (for battery sites) |
| Secure cloud connection | Hardware TLS acceleration |
| Small form factor | 25mm x 18mm module |
| Low cost | ~$3 per module |
| OTA updates | Dual OTA partitions with rollback |

# 3. Hardware Components

## Bill of Materials

| Component | Model | Purpose | Cost (approx) |
| --- | --- | --- | --- |
| MCU | ESP32-WROOM-32 (4MB Flash) | Main controller | $3 |
| RS485 Transceiver | MAX485 / SP485 | Modbus communication | $0.50 |
| 4G Modem | SIM A7670C | Cellular connectivity | $8 |
| SD Card Module | SPI SD Card adapter | Offline data storage | $1 |
| RTC | DS3231 (I2C) | Accurate timestamps | $1 |
| Status LEDs | 3x LEDs (Green/Blue/Red) | Visual status | $0.10 |
| Power Supply | 5V/2A USB or DC adapter | System power | $2 |

Total BOM cost: ~$15-16 per unit

## Complete GPIO Pin Map

ESP32 GPIO Allocation (19 pins used, 0 conflicts)
═══════════════════════════════════════════════════
 GPIO 0  │ BOOT button (input, pull-up)
 GPIO 2  │ SIM A7670C Reset (output)
 GPIO 4  │ SIM A7670C Power Key (output)
 GPIO 5  │ SD Card CLK (SPI VSPI)
 GPIO 15 │ SD Card CS (SPI chip select)
 GPIO 16 │ RS485 RX (UART2 RX)
 GPIO 17 │ RS485 TX (UART2 TX)
 GPIO 18 │ RS485 RTS/DE (direction control)
 GPIO 19 │ SD Card MISO (SPI)
 GPIO 21 │ DS3231 RTC SDA (I2C)
 GPIO 22 │ DS3231 RTC SCL (I2C)
 GPIO 23 │ SD Card MOSI (SPI)
 GPIO 25 │ Web Server LED (active low)
 GPIO 26 │ MQTT Connection LED (active low)
 GPIO 27 │ Sensor Read LED (active low)
 GPIO 32 │ SIM A7670C TX → ESP32 RX (UART1)
 GPIO 33 │ ESP32 TX → SIM A7670C RX (UART1)
 GPIO 34 │ Config button (input-only, pull-down)
═══════════════════════════════════════════════════

## Wiring Diagram

┌──────────────────────────┐
                         │      ESP32-WROOM-32      │
                         │                          │
   [Dalian Flow Meter]   │    GPIO 16 ◄── RX       │   [SIM A7670C]
   [Aquadax Quality ]───►│    GPIO 17 ──► TX       │   GPIO 32 ◄── TX
   [Opruss Ace      ]    │    GPIO 18 ──► RTS/DE   │   GPIO 33 ──► RX
        RS485 Bus         │                          │   GPIO 2  ──► RESET
                         │    GPIO 21 ◄──► SDA     │   GPIO 4  ──► PWRKEY
   [DS3231 RTC]─────────►│    GPIO 22 ──► SCL      │
                         │                          │   [Status LEDs]
   [SD Card Module]      │    GPIO 5  ──► CLK      │   GPIO 25 ──► Web LED
                    ◄───►│    GPIO 15 ──► CS       │   GPIO 26 ──► MQTT LED
                         │    GPIO 19 ◄── MISO     │   GPIO 27 ──► Sensor LED
                         │    GPIO 23 ──► MOSI     │
                         │                          │   [Buttons]
                         │    GPIO 34 ◄── Config   │   GPIO 0  ◄── BOOT
                         └──────────────────────────┘

# 4. Software Architecture

## Technology Stack

| Layer | Technology |
| --- | --- |
| OS | FreeRTOS (real-time operating system) |
| Framework | ESP-IDF v5.5.1 (Espressif IoT Development Framework) |
| Language | C (25,787 lines) |
| Cloud Protocol | MQTT over TLS 1.2 |
| Sensor Protocol | Modbus RTU over RS485 (UART) |
| Cellular | PPP (Point-to-Point Protocol) over AT commands |
| Storage | FAT32 filesystem on SD card, NVS Flash for config |
| Web Server | ESP HTTP Server (embedded HTML/JS/CSS) |

## FreeRTOS Task Architecture

┌─────────────────────────────────────────────────────────┐
│                    ESP32 Dual Core                       │
├──────────────────────┬──────────────────────────────────┤
│      CORE 0          │           CORE 1                 │
│                      │                                   │
│  ┌────────────────┐  │  ┌────────────────┐              │
│  │  Modbus Task   │  │  │  MQTT Task     │              │
│  │  Priority: 5   │  │  │  Priority: 4   │              │
│  │  Stack: 8KB    │  │  │  Stack: 8KB    │              │
│  │                │  │  │                │              │
│  │  - Serial TEST │  │  │  - Connect to  │              │
│  │    command      │  │  │    Azure IoT   │              │
│  │  - Monitor     │  │  │  - SAS token   │              │
│  │    shutdown     │  │  │  - Reconnect   │              │
│  └────────────────┘  │  │  - Device Twin │              │
│                      │  └────────────────┘              │
│                      │                                   │
│                      │  ┌────────────────┐              │
│                      │  │ Telemetry Task │              │
│                      │  │  Priority: 3   │              │
│                      │  │  Stack: 12KB   │              │
│                      │  │                │              │
│                      │  │  - Read sensors│              │
│                      │  │  - Build JSON  │              │
│                      │  │  - Send MQTT   │              │
│                      │  │  - SD caching  │              │
│                      │  │  - SD replay   │              │
│                      │  └────────────────┘              │
│                      │                                   │
│  ┌─────────────────────────────────────────┐            │
│  │         Main Task (app_main)            │            │
│  │  - Web server toggle (GPIO 34)          │            │
│  │  - LED status updates                   │            │
│  │  - Watchdog feeding                     │            │
│  │  - Heartbeat logging                    │            │
│  │  - Telemetry timeout recovery           │            │
│  └─────────────────────────────────────────┘            │
│                                                          │
│  ┌────────────────┐  ┌─────────────────┐               │
│  │ Memory Monitor │  │ Modem Reset     │               │
│  │ Priority: 1    │  │ Priority: 2     │               │
│  │ Heap tracking  │  │ On-demand only  │               │
│  └────────────────┘  └─────────────────┘               │
└─────────────────────────────────────────────────────────┘

## Source Code Structure

main/
├── main.c               │ 5000+ lines │ FreeRTOS tasks, telemetry, MQTT, SD replay
├── web_config.c          │ 11000+ lines│ Web UI (HTML/JS/CSS embedded in C strings)
├── web_config.h          │ 250 lines  │ Configuration structures and constants
├── web_assets.h          │ 200 lines  │ HTML header, navigation menu
├── sensor_manager.c      │ 1200 lines │ Modbus reads, byte order decode
├── sensor_manager.h      │ 80 lines   │ Sensor data structures
├── modbus.c              │ 400 lines  │ RS485 UART, CRC16, Modbus RTU
├── modbus.h              │ 50 lines   │ Modbus function definitions
├── sd_card_logger.c      │ 800 lines  │ SD card operations, mutex, retry
├── sd_card_logger.h      │ 60 lines   │ SD card API
├── a7670c_ppp.c          │ 900 lines  │ SIM module AT commands, PPP
├── a7670c_ppp.h          │ 80 lines   │ Modem configuration structures
├── a7670c_http.c         │ 200 lines  │ HTTP over cellular
├── ds3231_rtc.c          │ 300 lines  │ RTC I2C driver
├── json_templates.c      │ 400 lines  │ Telemetry JSON builders
├── ota_update.c          │ 500 lines  │ GitHub OTA with redirect handling
├── iot_configs.h         │ 40 lines   │ Version, timeouts, Azure defaults
└── gpio_map.h            │ 50 lines   │ Pin definitions

# 5. Features - Complete List

## Core Features

| # | Feature | Description |
| --- | --- | --- |
| 1 | **Modbus RTU Communication** | Read any RS485 Modbus sensor (holding/input registers, function codes 0x03/0x04) |
| 2 | **Azure IoT Hub Integration** | MQTT over TLS with SAS token authentication |
| 3 | **Dual Connectivity** | WiFi (STA mode) OR 4G Cellular (A7670C PPP) |
| 4 | **SD Card Offline Caching** | Store telemetry when internet is down, auto-replay when it returns |
| 5 | **Web Configuration UI** | Full web interface on SoftAP (192.168.4.1) for field setup |
| 6 | **OTA Firmware Updates** | Over-the-air updates from GitHub releases via Azure Device Twin |
| 7 | **Device Twin** | Remote configuration and monitoring from Azure cloud |
| 8 | **Watchdog Timer** | 120-second hardware watchdog prevents system hangs |
| 9 | **RTC Timestamps** | DS3231 provides accurate timestamps even without NTP |
| 10 | **Status LEDs** | Visual indicators for Web Server, MQTT, Sensor status |

## Sensor Features

| # | Feature | Description |
| --- | --- | --- |
| 11 | **Auto-detect byte order** | Configurable: ABCD, CDAB, BADC, DCBA for different meter brands |
| 12 | **Multiple data types** | UINT16, UINT32, INT32, FLOAT32, and custom fixed formats |
| 13 | **Scale factors** | Multiply raw register values by configurable factor |
| 14 | **Quality sensors** | Multi-parameter: pH, TDS, Temp, Humidity, TSS, BOD, COD |
| 15 | **Pre-configured sensors** | Built-in profiles for Dalian, Clampon, Piezometer, Aquadax, Opruss, Aster |
| 16 | **Modbus Explorer** | Live register reading tool in web UI for debugging |
| 17 | **Write registers** | Write single or multiple Modbus registers from web UI |
| 18 | **Modbus scan** | Scan bus for connected slave devices |

## Reliability Features

| # | Feature | Description |
| --- | --- | --- |
| 19 | **SD card retry logic** | 3 retries with increasing delays for transient I/O errors |
| 20 | **RAM buffer fallback** | 3-message RAM buffer when SD card fails completely |
| 21 | **Auto SD recovery** | Periodic recovery attempts every 60 seconds |
| 22 | **MQTT reconnection** | Exponential backoff (10s → 30s → 60s → 120s → 180s) |
| 23 | **Telemetry timeout** | Force restart after 30 min without telemetry (skipped if SD caching) |
| 24 | **Modem reset** | Automatic power cycle of SIM module on connectivity failure |
| 25 | **Memory monitor** | Tracks heap usage, warns at 30KB, critical at 20KB |
| 26 | **Heartbeat logging** | System health logged to SD card every 5 minutes |
| 27 | **OTA rollback** | Automatic rollback if new firmware fails to boot |

## Web Interface Features

| # | Feature | Description |
| --- | --- | --- |
| 28 | **System Overview** | Heap, uptime, MQTT status, sensor count |
| 29 | **Sensor Configuration** | Add/edit/delete sensors with full Modbus parameters |
| 30 | **Azure Settings** | Configure IoT Hub, device ID, device key |
| 31 | **Network Settings** | WiFi SSID/password, SIM APN configuration |
| 32 | **SD Card Management** | View status, clear data, trigger replay |
| 33 | **RTC Configuration** | View/set time, sync with NTP |
| 34 | **Modbus Explorer** | Read/write any register on any slave |
| 35 | **OTA Management** | Trigger firmware update, view progress |
| 36 | **System Controls** | Reboot, watchdog control, GPIO trigger |
| 37 | **SIM Test** | Test cellular connectivity with status polling |

# 6. Supported Sensors

## Flow Meters

| Sensor | Data Format | Registers | Default Baud | Notes |
| --- | --- | --- | --- | --- |
| Dalian Ultrasonic | UINT32 (3412) | 2 regs from addr 0 | 9600 | Most common deployment |
| Clampon | FLOAT32 | 2 regs | 9600 | Clamp-on ultrasonic |
| Piezometer / Hydrostatic | FLOAT32 | 2 regs | 9600 | Level measurement with tank height calculation |
| Generic Flow | Configurable | Configurable | 9600/19200 | Any Modbus RTU flow meter |

## Water Quality Sensors

| Sensor | Parameters | Registers | Byte Order | Function Code |
| --- | --- | --- | --- | --- |
| Aquadax | pH, TDS, Temp, Humidity, TSS, BOD, COD | 12 from addr 1280 | CDAB + byte-swap | 0x03 |
| Opruss Ace | pH, Temp, Humidity | 22 from addr 0 | CDAB (word-swap) | 0x03 |
| Opruss Ace TDS | TDS, Temperature | 2+2 from addr 0x16/0x20 | DCBA (byte+word swap) | 0x04 |
| Aster | pH, TDS | UINT16 at reg 6 + slave 2 reg 0 | Standard | 0x03 |

## How Sensor Data Flows

Sensor Register → Modbus RTU → Raw Bytes → Byte Order Decode → Scale Factor → JSON → MQTT → Azure
     0x6804          [02 03 04         [0x68, 0x04,     UINT32: 1337348      ×1.0    {"unit_id":"FG24027F",
     0x0014           68 04 00 14]      0x00, 0x14]                                     "params_data":{"totalizer":
                                                                                         "1337348"},"created_on":
                                                                                         "2026-03-13T10:30:00Z"}

# 7. Cloud Integration - Azure IoT Hub

## Connection Architecture

ESP32 Gateway                              Azure IoT Hub
     │                                          │
     ├── MQTT Connect ──────────────────────── │ (TLS 1.2, port 8883)
     │   Username: hub.azure-devices.net/       │
     │             device-id/?api-version=...   │
     │   Password: SharedAccessSignature ...    │
     │                                          │
     ├── Publish Telemetry ─────────────────── │ Topic: devices/{id}/messages/events/
     │   {"unit_id":"FG24027F",                │
     │    "params_data":{"totalizer":"1337348"},│
     │    "created_on":"2026-03-13T10:30:00Z"} │
     │                                          │
     ├── Subscribe Device Twin ◄───────────── │ Desired properties (cloud → device)
     │   telemetry_interval, ota_url,           │   - Change settings remotely
     │   reboot_device, maintenance_mode        │   - Trigger OTA updates
     │                                          │
     └── Report Device Twin ────────────────── │ Reported properties (device → cloud)
         firmware_version, free_heap,           │   - Device status monitoring
         uptime, sensor_count, mqtt_reconnects  │   - Remote diagnostics

## Telemetry JSON Format

Single Flow Meter:

{
  "unit_id": "FG24027F",
  "params_data": {
    "totalizer": "1337348"
  },
  "created_on": "2026-03-13T10:30:00Z"
}

Water Quality Sensor (Aquadax):

{
  "unit_id": "TFG2235Q",
  "params_data": {
    "pH": "7.20",
    "TDS": "245.00",
    "Temp": "28.50",
    "HUMIDITY": "65.00",
    "TSS": "12.00",
    "BOD": "8.50",
    "COD": "15.00"
  },
  "type": "QUALITY",
  "created_on": "2026-03-13T10:30:00Z"
}

## Device Twin Properties

Desired (Cloud → Device):

| Property | Type | Description |
| --- | --- | --- |
| telemetry_interval | int | Seconds between readings (default: 300) |
| modbus_retry_count | int | Retries per Modbus read (default: 2) |
| modbus_retry_delay | int | ms between retries (default: 100) |
| web_server_enabled | bool | Start/stop web server remotely |
| maintenance_mode | bool | Pause telemetry for maintenance |
| reboot_device | bool | Trigger remote reboot |
| ota_url | string | Firmware URL for OTA update |
| ota_enabled | bool | Allow/block OTA updates |

Reported (Device → Cloud):

| Property | Example | Description |
| --- | --- | --- |
| firmwareVersion | "1.3.7" | Current firmware |
| freeHeapBytes | 88544 | Available RAM |
| uptimeSeconds | 714243 | Seconds since boot |
| telemetrySentCount | 4645 | Total messages sent |
| networkMode | "SIM" | WiFi or SIM |
| sensors | [{name, unit_id, type}] | Connected sensor list |
| ota.status | "idle" | OTA progress |

# 8. Web Configuration Interface

## How to Access

Press GPIO 34 button (or connect GPIO 34 to 3.3V)

ESP32 creates WiFi hotspot: ModbusIoT-Config (password: config123)

Connect phone/laptop to this WiFi

Open browser: http://192.168.4.1

## Interface Sections

| Section | Purpose | Key Actions |
| --- | --- | --- |
| System Overview | Dashboard with heap, uptime, MQTT, sensors | View system health |
| Modbus Sensors | Configure flow meters and quality sensors | Add/edit/delete/test sensors |
| Azure IoT Hub | Cloud connection settings | Set device ID, key, hub FQDN |
| Network Settings | WiFi and SIM configuration | Set SSID, password, APN |
| SD Card | Offline storage management | View status, clear, replay |
| RTC Clock | Real-time clock settings | Sync time, set manually |
| Modbus Explorer | Advanced register read/write | Debug sensor communication |
| OTA Update | Firmware management | Trigger update, view progress |
| System Controls | Device management | Reboot, watchdog, GPIO |

## Technical Details

Built as embedded HTML/JS/CSS inside C strings (web_config.c, 609KB)

Uses chunked HTTP response for streaming large pages

Each section sent via `httpd_resp_sendstr_chunk()`

51 URI handlers registered for all endpoints

Web server runs on SoftAP (192.168.4.1) alongside normal WiFi STA

# 9. Connectivity - WiFi & 4G Cellular

## WiFi Mode

ESP32 connects as WiFi Station (STA) to existing router
├── Gets IP via DHCP
├── DNS: 8.8.8.8 (primary), 8.8.4.4 (backup)
├── Reconnect logic: 5 attempts, then periodic retry every 30s
└── Can also run SoftAP simultaneously for web configuration

## 4G Cellular Mode (SIM A7670C)

ESP32 ──UART1──► A7670C ──4G LTE──► Internet ──► Azure IoT Hub
         │
         ├── AT commands for modem control
         ├── PPP (Point-to-Point Protocol) for IP connectivity
         ├── Signal strength monitoring (AT+CSQ)
         ├── Automatic modem power cycling on failure
         └── Exponential backoff for retries

AT Command Sequence:

`AT` - Check modem alive

`AT+CFUN=1` - Enable radio

`AT+CPIN?` - Check SIM card

`AT+CSQ` - Signal strength

`AT+CGDCONT=1,"IP","APN"` - Set APN

`ATD*99#` - Dial PPP connection

PPP negotiation → IP address → Internet access

## Mode Selection

Configured via web UI under Network Settings

WiFi mode: faster, cheaper, for sites with router

SIM mode: works anywhere with cellular coverage

Can switch between modes without reflashing

# 10. Offline Data Storage - SD Card

## How It Works

Normal Operation:                    Offline Operation:
  Sensor → JSON → MQTT → Azure        Sensor → JSON → SD Card
                                                         │
                                       When internet returns:
                                         SD Card → MQTT → Azure
                                         (chronological order)

## Key Features

| Feature | Detail |
| --- | --- |
| File format | JSON lines in `/sdcard/telemetry_messages.txt` |
| Max messages | Limited by SD card size (typically 1000s) |
| Replay order | Chronological (oldest first) |
| Rate limiting | 500ms between messages, 10 per batch, 2s between batches |
| Error handling | 3 retries, RAM fallback (3 messages), auto-recovery every 60s |
| Thread safety | Mutex on every SD card operation |
| Corruption detection | Invalid JSON auto-deleted during replay |
| Power-loss protection | `CONFIG_FATFS_IMMEDIATE_FSYNC` enabled |

## SD Card Hardware

| Pin | GPIO | Function |
| --- | --- | --- |
| CLK | 5 | SPI Clock |
| MOSI | 23 | Data out |
| MISO | 19 | Data in |
| CS | 15 | Chip select |

SPI frequency: 1MHz (conservative for reliability)

# 11. OTA Firmware Updates

## How OTA Works

1. Admin sets ota_url in Azure Device Twin
   └── "https://github.com/.../releases/download/v1.3.8/mqtt_azure_minimal.bin"

2. Device receives Device Twin update
   └── Detects new ota_url

3. Device downloads firmware
   ├── Stops MQTT to free ~30KB heap
   ├── Follows GitHub redirects manually (streaming API limitation)
   ├── Skips certificate verification for GitHub CDN
   └── Writes to inactive OTA partition

4. Device reboots to new firmware
   ├── If boot succeeds → marks partition as valid
   └── If boot fails → automatic rollback to previous version

## Partition Layout (FROZEN since v1.3.7)

Flash Address Map (4MB Total):
┌──────────────┬─────────┬──────────┐
│ 0x001000     │ Bootloader          │ ~26KB
├──────────────┤                     │
│ 0x008000     │ Partition Table     │ 4KB
├──────────────┤                     │
│ 0x009000     │ NVS (config)        │ 40KB ◄── Expanded in v1.3.7
├──────────────┤                     │
│ 0x013000     │ PHY Init            │ 4KB
├──────────────┤                     │
│ 0x014000     │ OTA Data            │ 8KB
├──────────────┤                     │
│ 0x020000     │ OTA_0 (app slot 1)  │ 1.5MB ◄── Active firmware
├──────────────┤                     │
│ 0x200000     │ OTA_1 (app slot 2)  │ 1.5MB ◄── Update target
├──────────────┤                     │
│ 0x3E0000     │ Storage (FAT)       │ 128KB
└──────────────┴─────────────────────┘

CRITICAL: This partition table is FROZEN. OTA cannot change it. Any change requires physical access to all deployed devices.

# 12. Development Timeline

## Phase 1: Foundation (Nov 2025)

Initial ESP32 project setup with ESP-IDF

Basic Modbus RTU communication (UART2)

WiFi STA mode connection

Azure IoT Hub MQTT integration

Basic web configuration page

## Phase 2: SIM & Connectivity (Nov-Dec 2025)

A7670C 4G LTE modem integration (PPP)

Dual mode: WiFi OR SIM selectable

SIM test functionality in web UI

DNS resolution fixes for both modes

Modem power-on sequencing and debug logging

## Phase 3: Reliability & Storage (Dec 2025)

SD card offline caching implementation

Automatic replay when connectivity returns

DS3231 RTC integration for accurate timestamps

NTP time sync with RTC fallback

SD card corruption detection and cleanup

## Phase 4: Sensor Expansion (Dec 2025 - Jan 2026)

ZEST sensor support and byte order fixes

Flow meter pre-configured profiles (Dalian, Clampon)

Piezometer/Hydrostatic level sensor

Generic configurable sensor type

Scale factor and register count configuration

## Phase 5: Web Interface Enhancement (Jan 2026)

Modern responsive web UI redesign

Mobile-friendly forms and layouts

Modbus Explorer for live register reading

Write single/multiple registers

Modbus bus scan functionality

Real-time system status monitoring

## Phase 6: Water Quality Sensors (Jan-Feb 2026)

Aquadax 7-parameter water quality sensor

Opruss Ace 3-parameter sensor

Opruss Ace TDS (separate slave, different byte order)

Quality sensor telemetry JSON format

Multi-parameter display cards in web UI

## Phase 7: Cloud Management (Feb 2026)

Azure Device Twin (desired + reported properties)

Remote telemetry interval configuration

Remote OTA trigger via Device Twin

Remote reboot, maintenance mode, web server control

OTA from GitHub releases with redirect handling

## Phase 8: Production Hardening (Feb-Mar 2026)

Memory optimization (~20KB heap saved)

SD card retry logic (3 retries + RAM fallback)

Watchdog timer (120s) and telemetry timeout (30min)

Modem auto-reset on connectivity failure

Heartbeat logging to SD card

SPI bus leak fix on SD mount failure

Stack overflow fix for web server start

## Phase 9: New Sensors & Testing Tools (Mar 2026)

Aster pH/TDS water quality sensor

Auth/WebSocket/provisioning removal (binary size)

Serial TEST command for instant RS485 verification

Batch PCB board testing tool (board_tester.py)

SIM A7670C PCB integration analysis

# 13. Bugs Fixed & Lessons Learned

## Critical Bugs Fixed (13 major issues)

| # | Bug | Root Cause | Impact | Fix |
| --- | --- | --- | --- | --- |
| 1 | ZEST sensor wrong value (2,818,048 vs 43) | Missing data type handler | Wrong readings | Added ZEST_FIXED handler |
| 2 | WiFi/SIM sections disappear from web UI | Code deletion during corruption fix | No configuration | Re-added sections |
| 3 | JavaScript null errors in web UI | Missing HTML elements | Page broken | Added all referenced IDs |
| 4 | GPIO conflict false positives | Aggressive compile-time checks | Build fails | Documented real conflicts |
| 5 | MQTT reconnection crashes | Low retry limit + restart enabled | Device reboots | 20 retries, disabled restart |
| 6 | OTA from GitHub fails | Cert, heap, redirect, buffer issues | No remote updates | 5 separate fixes |
| 7 | Data loss during SD replay | Replay blocks sensor reading | 4+ hours no data | Pause replay for readings |
| 8 | OTA fails after partition change | Partition table changed in v1.3.7 | All devices need reflash | Froze partition table |
| 9 | SD cached messages wrong timestamp | Payload copy inside if(connected) | All same timestamp | Moved copy outside if |
| 10 | SD I/O errors cause data loss | No retry, no fallback | Messages lost | 3 retries + RAM buffer |
| 11 | Restart after 30min WiFi disconnect | Timeout doesn't check SD | Unnecessary reboot | Skip if SD caching |
| 12 | SD fails after restart - SPI leak | SPI bus not freed on mount fail | Permanent SD failure | Added spi_bus_free() |
| 13 | Stack overflow starting web server | Main task 3.5KB, 51 URI handlers | Crash | Increased to 8KB |

## Key Lessons Learned

Modbus byte order: NEVER trust sensor documentation labels. Always verify with raw hex values against display reading.

Static buffers: Always update output buffers regardless of connection state. Don't put buffer updates inside conditional blocks.

Thread safety: Acquire mutex at start, release before EVERY return path. Never hold mutex during vTaskDelay.

Web server TCP: Each `httpd_resp_sendstr_chunk()` = 1 TCP round trip. Combine into fewest sends possible.

Partition table: Plan partition sizes generously from day one. Once deployed, you can never change them via OTA.

Azure JSON format: unit_id MUST be first field. No "type" field for flow meters. Values MUST be strings. Batch sends bare array, not wrapped object.

sdkconfig vs defaults: Always verify settings in sdkconfig, not sdkconfig.defaults. The sdkconfig file takes precedence.

# 14. Production Deployment

## Device: sssh_24

| Field | Value |
| --- | --- |
| Device ID | sssh_24 |
| Location | Residential Overhead Tank (OHT) |
| Network | 4G Cellular (SIM A7670C) |
| Firmware | v1.3.7 |
| Uptime | 8+ days (as of March 13, 2026) |
| Messages Sent | 4,645 |
| Telemetry Failures | 0 (current session) |
| Restart Count | 35 (lifetime) |
| Free Heap | 86KB |
| Min Free Heap | 74KB |
| SD Card | Enabled, active |

## Connected Sensors

| Sensor | Unit ID | Slave ID | Type |
| --- | --- | --- | --- |
| Residential OHT Inlet | FG24027F | 1 | Flow Meter |
| Residential OHT Outlet | FG24028F | 2 | Flow Meter |

## Azure IoT Hub

Hub: fluxgen-testhub.azure-devices.net

Authentication: SAS token

Telemetry interval: 300 seconds (5 minutes)

Device Twin: Active, version 56946

OTA: Enabled, pending v1.3.8 update

# 15. Production Board Testing Tool

## Purpose

Before shipping new PCB boards, we need to verify RS485 Modbus communication works on every board. Manual testing is slow and error-prone.

## Solution: board_tester.py

A Python script that uses one pre-flashed ESP32 module to test unlimited PCBs.

## How It Works

1. Flash ESP32 once with firmware + configure sensor
2. Place ESP32 on new PCB
3. Connect Dalian flow meter (reference sensor)
4. Run: python board_tester.py batch --port COM5
5. Press Enter → "TEST" sent via USB serial
6. ESP32 reads sensor → PASS/FAIL in 3 seconds
7. Move to next PCB, repeat

## Firmware Integration

Added to modbus_task in main.c:

UART0 driver installed for reading serial commands

When "TEST" received → calls `sensor_read_all_configured()`

Prints `[RS485_TEST] PASS` or `[RS485_TEST] FAIL`

## Script Features

3 automatic retries per board

Auto-detects boot state (works during or after boot)

Results logged to CSV: `rs485_test_results.csv`

Batch mode for testing many boards in sequence

Detailed failure diagnostics

## Test Output Example

TESTING: PCB-001  (up to 3 attempts)
  Attempt 1: sending TEST (waiting for ESP32)...
  [10.1s] [RS485_TEST] Serial test command received - reading sensors NOW
  [11.2s] [RECV] Received 9 bytes from RS485
  [11.2s] [DATA] Register[0]: 0x6804 (26628)
  [11.2s] [RS485_TEST] PASS: Read 1/1 sensors successfully

  ╔═════════════════════════════════════════╗
  ║   PASS        PCB-001   RS485 OK       ║
  ╚═════════════════════════════════════════╝

# 16. PCB Design - SIM Module Integration

## Objective

Integrate the SIM A7670C 4G LTE module directly onto our custom PCB instead of using a separate development board.

## Module Specifications

| Parameter | Value |
| --- | --- |
| Module | SIM A7670C-LNNV (Industrial Grade) |
| Type | Cat 1 4G LTE + 2G GSM Dual-Mode |
| Size | 56mm x 56mm (development board) |
| Interface | UART (3.3V TTL), SPI, I2C |
| Power | 3.3V-4.2V DC, 2A peak during TX |
| SIM | Nano-SIM slot (onboard) |
| Antenna | Onboard PCB antenna + external SMA option |

## PCB Design Requirements

| Requirement | Specification |
| --- | --- |
| Power trace | 1mm+ width (2A peak) |
| Bulk capacitor | 470uF Low-ESR near VDD pin |
| Decoupling | 100uF + 10uF ceramic |
| Ground plane | Solid copper pour under module |
| Antenna clearance | 10mm from copper/traces |
| Module placement | Board edge, antenna outward |
| RESET pull-up | 10K to 3.3V |
| Mounting | 4x M3 holes, 48.40mm spacing |

## KiCad Footprint

Available in repository: SIM-A7670C---4G-LTE-Modem/Footprint/A7670C Module.pretty.zip

# 17. Performance & Memory

## Heap Memory Budget

Total Available RAM: ~300KB
├── FreeRTOS + ESP-IDF overhead: ~150KB
├── Application allocations: ~60KB
└── Free for operations: ~90KB (web off) / ~60KB (web on)

Warning threshold:  30KB free
Critical threshold: 20KB free
Emergency:          10KB free

## Memory Optimizations (v1.3.8)

| Optimization | Savings |
| --- | --- |
| Max sensors 15 → 10 | ~9KB (array reductions) |
| Static buffer reductions | ~4KB |
| Task stack reductions | ~4KB |
| Config reductions | ~1KB |
| Telemetry payload 4096 → 2560 | ~1.5KB |
| Eliminated batch_payload malloc | ~0.5KB |
| **Total saved** | **~20KB** |

## Typical Performance

| Metric | Value |
| --- | --- |
| Boot to first telemetry | ~25 seconds |
| Modbus read (single sensor) | ~1 second |
| MQTT publish | ~100ms (WiFi), ~500ms (4G) |
| SD card write | ~50ms |
| Web page load | ~3-5 seconds (125KB HTML) |
| OTA download | ~3-5 minutes (1.5MB firmware) |

# 18. Technical Constraints

| Constraint | Impact | Mitigation |
| --- | --- | --- |
| 4MB Flash | Limited firmware + OTA size | Two 1.5MB OTA slots, code optimization |
| ~300KB RAM | Limited concurrent operations | Memory monitoring, buffer reductions |
| Partition table frozen | Cannot change flash layout via OTA | Planned generously in v1.3.7 |
| 609KB web_config.c | Fragile to edit, slow compilation | Future: split into separate files |
| 1.5MB OTA partition | Binary must stay under this | Removed unused features to fit |
| 10 max sensors | Hardware limitation for memory | Sufficient for current deployments |
| Single UART for Modbus | One RS485 bus | All sensors share the bus |
| ESP32 single-precision float | Limited decimal precision | String formatting for telemetry |

# 19. Security

| Feature | Implementation |
| --- | --- |
| Cloud transport | MQTT over TLS 1.2 (port 8883) |
| Authentication | Azure SAS tokens (HMAC-SHA256) |
| Token expiry | 1 hour, auto-renewal |
| Certificate validation | ESP x509 certificate bundle |
| WiFi | WPA2-PSK |
| Web UI | SoftAP only (not exposed to internet) |
| OTA | HTTPS from GitHub (certificate bundle) |
| NVS | Encrypted storage for credentials |

# 20. Testing

## Manual Testing

Serial monitor verification of Modbus reads

Web UI functional testing in browser

MQTT message verification in Azure IoT Explorer

SD card caching/replay verification

OTA update end-to-end test

WiFi and SIM mode switching

## Automated Testing

`board_tester.py` - RS485 hardware verification

`quick_rs485_test.py` - HTTP-based sensor test

`modbus_simulator.py` - pymodbus RTU simulator

`serial_monitor.py` - Serial output parser

`full_test_runner.py` - Complete test suite

## Test Infrastructure

tests/
├── board_tester.py          │ PCB RS485 batch tester
├── quick_rs485_test.py      │ HTTP endpoint tester
├── modbus_simulator.py      │ Modbus slave simulator
├── serial_monitor.py        │ Serial log parser
├── full_test_runner.py      │ All-in-one test runner
├── config.py                │ Test configuration
└── rs485_test_results.csv   │ Test results log

# 21. Risk Assessment

| Risk | Likelihood | Impact | Mitigation | Status |
| --- | --- | --- | --- | --- |
| SD card failure | Medium | Data loss offline | 3-retry + RAM buffer + auto-recovery | Mitigated |
| Heap exhaustion | Low | Device crash/restart | Memory optimization + monitoring | Mitigated |
| OTA bricks device | Low | Need field visit | Dual partitions + rollback | Mitigated |
| 4G coverage gap | Medium | Temp offline | SD caching + auto-replay | Mitigated |
| Partition table change | Low | All devices reflash | Table frozen, plan around | Mitigated |
| Power loss during write | Low | SD corruption | IMMEDIATE_FSYNC enabled | Mitigated |
| Modbus bus contention | Low | Missed readings | Retry logic (3 attempts) | Mitigated |
| SAS token expiry | Low | MQTT disconnect | Auto-renewal every hour | Mitigated |
| 609KB web file corruption | Medium | Web UI broken | Careful editing, git backup | Acknowledged |

# 22. Future Roadmap

## Short Term (Next 2 Weeks)

| Task | Priority |
| --- | --- |
| Deploy v1.3.8 to production via OTA | High |
| Test new PCB boards with batch tester | High |
| Configure dev board with real Azure credentials | Medium |

## Medium Term (Next 1-2 Months)

| Task | Priority |
| --- | --- |
| SIM A7670C direct PCB integration | High |
| New PCB board design and fabrication | High |
| Field test Aster water quality sensor | Medium |
| Add more pre-configured sensor profiles | Medium |
| Implement batch telemetry mode | Medium |

## Long Term (3-6 Months)

| Task | Priority |
| --- | --- |
| Split web_config.c into separate files | Medium |
| Add MQTT over WebSocket option | Low |
| Edge computing (local alerts/rules) | Low |
| Multi-gateway coordination | Low |
| Battery-powered operation mode | Low |
| BLE configuration option | Low |

# 23. Project Metrics

| Metric | Value |
| --- | --- |
| **Development Duration** | 5 months (Nov 2025 - Mar 2026) |
| **Total Commits** | 255 |
| **Lines of Code** | 25,787 (C source in main/) |
| **Source Files** | 31 (.c and .h files) |
| **Features Delivered** | 37 major features |
| **Bugs Fixed** | 13 critical, 20+ minor |
| **Sensors Supported** | 9 types (5 flow + 4 quality) |
| **GPIO Pins Used** | 19 of 34 available |
| **Firmware Size** | ~1.1MB (within 1.5MB OTA limit) |
| **BOM Cost** | ~$15 per unit |
| **Production Devices** | 1 deployed (sssh_24) |
| **Uptime** | 8+ days continuous (current) |
| **Messages Delivered** | 4,645+ (zero failures) |
| **Board QC Test Time** | 3 seconds per board |

FluxGen Technologies | Industrial IoT Solutions

Report generated: March 26, 2026

FluxGen Technologies | Industrial IoT Solutions